SECTION 08 11 13 - HOLLOW METAL DOORS AND FRAMES

PART 1 - GENERAL

- SUMMARY

- Section Includes:

- Steel doors and frames for interior applications.

- Galvanized steel doors and frames for exterior applications.

- Door hardware preparation and reinforcement.

- Related Sections:

- Section 08 71 00 - Door Hardware.

- Section 09 91 00 - Painting.

- REFERENCES

- Reference Standards:

- ANSI/SDI A250.8 - Specifications for Standard Steel Doors and Frames.

- ANSI/SDI A250.4 - Test Procedure and Acceptance Criteria for Physical Endurance for Steel Doors.

- ASTM A653 - Standard Specification for Steel Sheet, Zinc-Coated.

- NFPA 80 - Standard for Fire Doors and Other Opening Protectives.

- SUBMITTALS

- Product Data: Submit manufacturer's technical data for each door and frame type.

- Include construction details, material gauges, and finishes.

- Include fire rating labels and certifications.

- Shop Drawings: Submit fabrication drawings for each door and frame assembly.

- Certifications: Submit fire rating certifications from testing laboratory.

- QUALITY ASSURANCE

- Fire-Rated Assemblies: Provide doors, frames, and hardware listed by UL or WHI.

- Manufacturer Qualifications: Minimum 10 years experience producing hollow metal products.

PART 2 - PRODUCTS

- MANUFACTURERS

- Acceptable Manufacturers:

- Ceco Door Products.

- Curries Company.

- Steelcraft.

- Republic Doors and Frames.

- Substitutions: In accordance with Section 01 60 00.

- STEEL DOORS

- Interior Doors (Type A):

- Construction: Full flush, seamless.

- Face Sheets: 16 gauge cold-rolled steel.

- Core: Honeycomb, polyurethane, or polystyrene.

- Level 3: Standard duty per ANSI/SDI A250.4.

- Physical performance: 250,000 cycles minimum.

- Fire-Rated Doors (Type B):

- Rating: As indicated on Drawings, 20 minutes to 3 hours.

- Construction: Comply with NFPA 80 requirements.

- Label: UL or WHI classification marking on door edge.

- Smoke seal: Intumescent seal at rated openings.

- STEEL FRAMES

- General: Full profile welded frames unless otherwise indicated.

- Material: 16 gauge steel minimum for door frames.

- Reinforcement: 7 gauge at hardware locations.

- Anchors: Provide anchors suitable for wall construction type.

PART 3 - EXECUTION

- EXAMINATION

- Verify wall openings are correct size and properly prepared.

- Verify wall construction is ready to receive frames.

- INSTALLATION

- Install doors and frames per SDI-117 and manufacturer's instructions.

- Set frames plumb, level, and square within 1/16 inch.

- Anchor frames securely to wall construction.

- Grouted frames: Fill completely with mortar.

- Drywall frames: Secure with appropriate anchors at 24 inches on center.

- Fire-rated assemblies: Install per listing requirements.

- ADJUSTING AND CLEANING

- Adjust hardware for proper operation.

- Clean surfaces and touch up damaged finishes.

- Remove and replace defective work.

END OF SECTION