SECTION 09 51 00 - ACOUSTIC CEILINGS

PART 1 - GENERAL

- SUMMARY

- Section Includes:

- Acoustic ceiling panels.

- Suspension systems for acoustic ceilings.

- Acoustic ceiling accessories.

- Related Sections:

- Section 09 22 16 - Non-Structural Metal Framing.

- Section 09 91 00 - Painting.

- REFERENCES

- Reference Standards:

- ASTM C635 - Standard Specification for Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-in Panel Ceilings.

- ASTM C636 - Standard Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels.

- ASTM E1264 - Standard Classification for Acoustical Ceiling Products.

- ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

- SUBMITTALS

- Product Data: Submit manufacturer's technical data for each product.

- Include performance characteristics and installation instructions.

- Include ceiling panel patterns and edge details.

- Samples: Submit two full-size samples of each ceiling panel type.

- Shop Drawings: Submit layout drawings showing panel arrangement and edge conditions.

- QUALITY ASSURANCE

- Fire Performance: Provide panels with Class A fire rating per ASTM E84.

- Seismic Requirements: Comply with ASCE 7 and CBC Chapter 13 for ceiling systems.

PART 2 - PRODUCTS

- MANUFACTURERS

- Acceptable Manufacturers:

- Armstrong World Industries.

- USG Corporation.

- CertainTeed Corporation.

- Substitutions: In accordance with Section 01 60 00.

- ACOUSTIC CEILING PANELS

- Standard Acoustic Panel (Type ACT-1):

- Size: 24 inches by 24 inches by 3/4 inch thick.

- NRC: 0.55 minimum.

- CAC: 35 minimum.

- Light Reflectance: 0.83 minimum.

- Edge Detail: Square lay-in.

- Color: White.

- High-NRC Acoustic Panel (Type ACT-2):

- Size: 24 inches by 48 inches by 3/4 inch thick.

- NRC: 0.70 minimum.

- CAC: 35 minimum.

- Edge Detail: Tegular.

- Application: Conference rooms and private offices.

- SUSPENSION SYSTEM

- Grid System: Heavy-duty exposed tee system per ASTM C635.

- Main Runners: 15/16 inch face width.

- Cross Tees: 15/16 inch face width, intermediate duty.

- Finish: White baked enamel to match ceiling panels.

- Hanger Wire: 12 gauge galvanized steel wire.

- Seismic Bracing: As required by code for Seismic Design Category D.

PART 3 - EXECUTION

- EXAMINATION

- Verify conditions are ready for ceiling installation:

- Structure is complete and accessible.

- MEP systems above ceiling are installed and tested.

- Room temperature and humidity are within manufacturer's limits.

- Do not proceed until unsatisfactory conditions are corrected.

- INSTALLATION

- Install suspension system per ASTM C636 and manufacturer's instructions.

- Install hanger wires at maximum 4 feet on center.

- Locate first hanger within 2 feet of each wall.

- Provide supplemental hangers at light fixtures and diffusers.

- Level grid to within 1/8 inch in 12 feet.

- Install seismic bracing per engineered drawings.

- Install ceiling panels after grid is complete and inspected.

- CLEANING AND PROTECTION

- Clean exposed surfaces of ceiling panels and grid.

- Replace panels that are damaged, soiled, or do not match.

- Protect installed ceilings from damage by other trades.

END OF SECTION