SECTION 22 40 00

PLUMBING FIXTURES

PART 1 - GENERAL

- SUMMARY

- Section Includes:

- Water closets.

- Lavatories.

- Sinks.

- Urinals.

- Drinking fountains/water coolers.

- Fixture supports and carriers.

- Wood blocking for wall-mounted fixtures.

- Related Sections:

- Section 22 05 00 - Common Work Results for Plumbing.

- Section 22 10 00 - Plumbing Piping (see Article 2.06 for trap requirements).

- Section 06 10 00 - Rough Carpentry: Wood blocking.

- REFERENCES

- Reference Standards:

- ASME A112.19.2 - Ceramic Plumbing Fixtures.

- ASME A112.19.3 - Stainless Steel Plumbing Fixtures.

- ASME A112.6.1M - Supports for Off-the-Floor Plumbing Fixtures. [VERIFY CURRENT EDITION]

- ADA Standards for Accessible Design.

- CBC Chapter 11B - Accessibility.

- California Green Building Standards Code (CALGreen) [If LEED: Also LEED v4.1 WE Credits].

- SUBMITTALS

- Product Data: Submit manufacturer's technical data for each fixture type.

- Include rated capacities, flow rates, and water consumption.

- Include rough-in dimensions and utility requirements.

- Show carrier rough-in dimensions.

- Show supply and waste connection locations.

- Include centerline dimensions.

- Include height above finished floor.

- Shop Drawings: Submit layout drawings for fixture installation.

- Show fixture locations and clearances.

- Show coordination with casework and accessories.

- Samples: Submit samples of fixture colors when requested by Architect.

- Sustainability Documentation: [COORDINATE WITH LEED CONSULTANT] Submit WaterSense certifications.

- QUALITY ASSURANCE

- Not Used.

- DELIVERY, STORAGE, AND HANDLING

- Deliver fixtures in manufacturer's original packaging.

- Store fixtures in clean, dry location protected from construction traffic.

- Handle fixtures carefully to avoid damage to surfaces and finishes.

- PROJECT CONDITIONS

- Verify rough-in dimensions and locations before fixture installation.

- Set fixtures level and plumb.

- New fixtures in renovated areas: Match existing.

PART 2 - PRODUCTS

- MANUFACTURERS

- Acceptable Manufacturers - Fixtures:

- American Standard.

- Kohler Co.

- TOTO USA.

- Sloan Valve/Zurn Industries (flush valves).

- Acceptable Manufacturers - Carriers:

- Jay R. Smith Mfg. Co.

- Josam Company.

- Wade.

- Substitutions: Other manufacturers may be considered if equal in quality.

- WATER CLOSETS

- Floor-Mounted Water Closet (WC-1):

- Type: Elongated bowl, floor-mounted, floor outlet.

- Flush Valve: Exposed, manual, 1.28 gpf.

- Seat: Open front, self-sustaining check hinge.

- Material: Solid plastic.

- Color: White.

- Wall-Hung Water Closet (WC-2): Accessible locations.

- Type: Elongated bowl, wall-hung, back outlet.

- Flush Valve: Concealed, sensor-operated, 1.28 gpf.

- Battery operated.

- Hardwired with battery backup.

- Coordinate power requirements with Electrical.

- Carrier: Adjustable, for 6-inch stud walls.

- Mounting Height: 17 inches to top of seat (ADA compliant).

- LAVATORIES

- Wall-Hung Lavatory (LAV-1):

- Type: Vitreous china, wall-hung.

- Size: 20 inches by 18 inches.

- Faucet Holes: 4-inch centers.

- Counter-Mounted Lavatory (LAV-2):

- Type: Vitreous china, self-rimming.

- Size: 20 inches by 17 inches oval.

- Faucets:

- Type: Single-handle, ceramic disc.

- Flow Rate: 0.5 gpm with laminar flow.

- Finish: Polished chrome.

- Supply Stops: Quarter-turn, chrome plated brass.

- Supply Risers: Braided stainless steel.

- Trap: See Section 22 10 00, Article 2.06.

- SINKS

- Service Sink (S-1):

- Type: Floor-mounted, enameled cast iron.

- Size: 24 inches by 20 inches by 10 inches deep.

- Rim Guard: Stainless steel. [CONFIRM WITH OWNER - THEY REJECTED LAST PROJECT]

- Break Room Sink (S-2):

- Type: Self-rimming, stainless steel.

- Size: 25 inches by 22 inches, single bowl.

- Gauge: 18 gauge, Type 304 stainless steel.

PART 3 - EXECUTION

- EXAMINATION

- Verify rough-in locations and dimensions before installation.

- Verify wall blocking is installed at proper locations and heights.

- Verify floor drains and waste connections are clear.

- INSTALLATION

- Install fixtures per manufacturer's instructions and referenced standards.

- Set fixtures level and plumb.

- Set fixtures in bed of plumber's putty or silicone sealant (white).

- Mounting Heights (to rim unless noted):

- Lavatories: 34 inches AFF.

- Accessible Lavatories: 34 inches AFF maximum.

- Water Closets: Per Article 2.02.

- Accessible Water Closets: 15 to 19 inches to top of seat.

- Urinals: 17 inches AFF (accessible); 24 inches AFF (standard).

- CONNECTIONS

- Connect fixtures to water supply and drainage systems.

- CLEANING

- Clean fixtures and fittings upon completion.

- Remove protective coverings and labels.

- Use non-abrasive cleaners approved by fixture manufacturer.

- Provide manufacturer's standard warranty for all fixtures.

END OF SECTION